## Definitions
1.1.1 PB Config Type Information
This field Type is used to configure the behaviour for a specific Push button. Multible informations can be retrieved from this field.
Button Type (bit 0):
· 0= Push Button
· 1= Switch
Destination (bit 1-7):
· 0 = destination is Not selected
· 1= destination is selected.
The following table shows the bit value for each destination:
Bit | Destination
1 | ZONE 1/ CHANNEL 1
2 | ZONE 2/ CHANNEL 2
3 | ZONE 3
4 | ZONE 4
5 | ZONE 5 / INTERNAL RELAY
6 | MUZ
7 | Not in Use
Sample: Config Type:0x09 = ButtonType=Switch and ZONE 4
Sample: Config Type:0x00 = Not Used/deleted
1.1.2 SW Profile Bits description
Ref 2 describes the SW profile bits for the GetSensorProfileReply and SetSensorProfile telegram.
1.1.3 User Config Bits
The table below describes the User Config bits for the GetUserConfigReply telegram.
Byte Field | Bit No | Bit field | Description
| 7 | RESERVED | Not Used
| 6 | RESERVED | Not Used
| 5 | RESERVED | Not Used
| 4 | RESERVED | Not Used
| 3 | RESERVED | Not Used
| 2 | CFG_INT_RELAY_LIGHTING | Internal Relay function (3 bits):
CFG_SYSTEM_COMMON_FUNC0 |  |  | 0=Internal relay is not in use.
1=Internal relay is used for Lighting
| 1 | CFG_INT_RELAY_HVAC | 2=Internal relay is used for HVAC
4=Internal relay is used for STDBY MIN
| 0 | CFG_INT_RELAY_STDBY_MIN
| 7 | CFG_WIRELESS_NEIGH_SLAVE
| 6 | CFG_WIRELESS_LINK_ENABLED | Wirless Master/Master functionality
| 5 | CFG_WIRELESS_SLAVE_ENABLED
| 4 | CFG_ECO_ENABLED
CFG_SYSTEM_COMMON_FUNC1 | 3 | CFG_WIRELESS_PB_ENABLED
| 2 | CFG_WALKTEST_ACTIVE | WalkTest function is running.
| 1 | CFG_YGM_INDICATION | YGM Indication is enabled.
| 0 | CFG_WALKTEST_MULTI_COLOR_LEDS | If set, the three PIR sensor will indicate using the LEDs which sector made the movement detection. NOTE: the use of this bit as to be approved by PM/UX!!!
Tunable White function:
| 7 | CFG_TW_DYNAMIC | 00= OOTB (Default Kelvin)
01= Tunable White Preset
10= Tunable White Dynamic
11= Tunable White Dynamic/Preset
| 6 | CFG_TW_DYNAMIC
| 5 | CFG_USR_DYN_SP_ACTIVE | User Dynamic Setpoint
CFG_SYSTEM_DALI_FUNC2 | 4 | RESERVED | Not Used
Dali Configuration:
| 3 | CFG_DALI_CONFIGURED | 0=BC
1=Addresseble
| 2 | CFG_BURNIN_ACTIVE
| 1 | CFG_EXT_HVAC_8HOUR_ACTIVE | 8 Hour function:
0=Not running (Done)
1=Running
| 0 | CFG_AUTO_ADD_1DEVICE | Auto Config function: From 02.18
0=Not running
1=Running
| 7 | RESERVED | Not Used
| 6 | CFG_AUTO_ON | Automatic On function selected by user.
| 5 | CFG_MANUAL_ON | Manual On function selected by user.
| 4 | CFG_MANUAL_OFF | Manual Off function selected by user.
CFG_ZONE_COMMON_FUNC1 | 3 | RESERVED | Not Used
| 2 | CFG_8HOUR_ACTIVE | 8-hour function active
| 1 | CFG_OVEREXP_ACTIVE
| 0 | CFG_DLC_ACTIVE
7
6
5
| 4 |  | Not Used
CFG_ZONE_COMMON_FUNC2 | 3 | RESERVED
2
1
0
| 7 | RESERVED | Not Used
| 6 | RESERVED | Not Used
| 5 | RESERVED | Not Used
| 4 | RESERVED | Not Used
CFG_ZONE_DALI_FUNC1 | 3 | RESERVED | Not Used
| 2 | RESERVED | Not Used
| 1 | RESERVED | Not Used
| 0 | RESERVED | Not Used
1.1.4 Wired PB Structure
The following table describes Configuration fields for Push Button configuration.
Field Offset | Field Size | Field
Description
0 | 1 | Config Type | Range (0..255)
See section 4.2.4 for a description of these fields.
1 | 1 | Function1 | Range (See section 4.2.3)
2 | 1 | Function2 | Range (See section 4.2.3)
3 | 1 | Param1 (for Function 1) | Range (0..255)
4 | 1 | Param2 (for Function 2) | Range (0..255)
1.1.5 Wireless Push Button Structure
The following table describes Configuration fields for wireless Push Buttons.
Field Offset | Field Size | Field
Description
0 | 3 | Button MAC-Addr. part. | the last 3 digits of the MAC address (??:??:??:XX:XX:XX)
3 | 5 | PB Structure A0 | See section 4.2.7 for a detailed description of PB Structure
8 | 5 | PB Structure A1 | See section 4.2.7 for a detailed description of PB Structure
13 | 5 | PB Structure B0 | See section 4.2.7 for a detailed description of PB Structure
18 | 5 | PB Structure B1 | See section 4.2.7 for a detailed description of PB Structure
1.1.6 Dali Push Button Structure
The following table describes Configuration fields for Dali Push Buttons.
Field Offset | Field Size | Field
Description
0 | 5 | PB Structure | See section 4.2.7 for a detailed description of PB Structure.
5 | 1 | Instance (0) | Range (0..15)
6 | 5 | PB Structure | See section 4.2.7 for a detailed description of PB Structure.
11 | 1 | Instance (3) | Range (0..15)
12 | 5 | PB Structure | See section 4.2.7 for a detailed description of PB Structure.
17 | 1 | Instance (6) | Range (0..15)
18 | 5 | PB Structure | See section 4.2.7 for a detailed description of PB Structure.
23 | 1 | Instance (7) | Range (0..15)
24 | 1 | Short Address | Range (0..63)
1.1.7 Tunable White Structure
The following table describes Configuration fields for Tunable White.
Field Offset | Field Size | Field
Description
0 | 2 | Kelvin | Range (2700K..6500K), 65535=No Change
2 | 2 | Lux Setting | Range (20..65535) Lux, 65535=No Change
States the Lux set point.

## Read_Write
1.1.1 0x010B - GetUserConfig
This telegram requests current Sensor Configuration for all zones. If this is the first time the App requests the configuration, then the sensor will reply with OOTB configuration.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetUserConfig Id
3 | 2 | Total Length | 0x07 | Total length of 7 bytes
5 | 2 | CRC16 | 0x847C | Calculated value, see section 4.5
1.1.2 0x010C - GetUserConfigReply
This telegram is a reply from GetUserConfig.
This Telegram must be able to handle up to 5 Zone definitions.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetUserConfigReply Id
3 | 2 | Total Length | 0xA7 | Total length of 167 bytes
5 | 2 | CRC16 | 0xC82F | Calculated value, see section 4.5
7 | 1 | CFG_VERSION | 0x0A | Indicates the version of the user config structure.
The version number is controlled by the sensor. Any time structural changes have been made to the user config structure, then the CFG_VERSION will be incremented.
Range (10)
8 | 1 | CFG_SYSTEM_CONFIGSTATE | 0x00 | Indicates the state of the User Configuration
0=Out Of The Box
1=FS_DK (Fact.Reset Denmark)
2=FS_SV (Fact.Reset Sweden)
3=FS_NO (Fact.Reset Norway)
4=FS_DE (Fact.Reset Germany)
5=FS_BE (Fact.Reset Belgium)
255=USER ( The user has made changes to the configuration)
9 | 1 | CFG_SYSTEM_NETWORK_ID | 0x00 | Identifies the ID of the BLE network
Range (0..253)=user network Id’s
10 | 1 | CFG_SYSTEM_COMMON_FUNC0 | 0x00
11 | 1 | CFG_SYSTEM_COMMON_FUNC1 | 0x00 | See section 4.2.6 for a detailed descr.
12 | 1 | CFG_SYSTEM_DALI_FUNC2 | 0x00
13 | 1 | CFG_SYSTEM_RESERVED1 |  | Not Used
14 | 1 | CFG_SYSTEM_RESERVED2 |  | Not Used
15 | 1 | CFG_V_PIRA | 0x00 | Indicates the sensitivity Level for Pir
0=OFF, 1=MIN,
16 | 1 | CFG_V_PIRB |  | 2=LOW, 3=HIGH,
17 | 1 | CFG_V_PIRC |  | 4=MAX
18 | 2 | CFG_T_SP |  | Indicate the time to recognize a short press.
ms. (150-10000)
500
1000
2000
20 | 2 | CFG_T_LP |  | Indicate the time to recognize a long press.
ms. (500-17000)
>CFG_T_SP
22 | 2 | CFG_T_VLP |  | Very long push timing.
ms. (10000-30000)
10500
11000
12000
24 | 2 | CFG_T_LP_FAIL |  | Long push fail time.
ms. (>=30001)
26 | 2 | CFG_T_HVACCON_DELAY |  | Indicate the time for the HVAC to turn On after motion detection
Sec. (120..7200)
28 | 2 | CFG_T_HVACOFF_DELAY |  | Indicate the time for the HVAC to turn Off after the last motion detection
Sec. (0..7200)
30 | 2 | CFG_T_STDBY_MIN_DELAY |  | Delay for Std.By Min.
Sec. (0..7200)
Zone 1
32 | 1 | CFG_ZONE_COMMON_FUNC1
33 | 1 | CFG_ZONE_ONOFF_FUNC2 |  | See section 4.2.6 for a detailed descr.
34 | 1 | CFG_ZONE_DALI_FUNC1
35 | 2 | CFG_ZONE_T_OFFPIR_DELAY |  | Range (1..65535) sec., Default: 15min
States the Off-Delay duration.
See section 4.2.1 for a detailed description of this field.
37 | 2 | CFG_ZONE_T_PRESENCE_DELAY |  | Range (1..65535) sec, Default: 15min
States the Presence-delay duration during 2-level control.
See section 4.2.1 for a detailed description of this field.
39 | 2 | CFG_ZONE_T_NON_PRESENCE_DELAY |  | Range (1..65535) sec., Default:65535
States the Non presence-delay duration during 2-level control.
See section 4.2.1 for a detailed description of this field.
41 | 2 | CFG_ZONE_T_ORIENTATION_DELAY |  | Range (0..65535) sec., Default: 10min
States the Orientation light Period.
43 | 2 | CFG_ZONE_T_ON_DELAY |  | Range (0..3600) sec.
States the delay after movement detection.
0 sec (no delay)
60 sec
120 sec
180 sec
240 sec
300 sec
45 | 1 | CFG_ZONE_TYPE |  | Range (0..4) enum.
Indicates the zone type.
0=Zone not used (disabled)
1=DLZ (Daylight zone)
2=SEZ (Secondary zone / OnOff zone)
3=MUZ (Multi zone)
4=HVAC (HVAC Control. OnOff Sensors
46 | 1 | CFG_ZONE_RESERVED |  | Not Used
47 | 2 | CFG_ZONE_DESKDAYLIGHTFACTORPCT |  | Range (0..1000) %
49 | 2 | CFG_ZONE_DESKMAXARTIFICIALLIGHT |  | Range (1..2000) Lux
51 | 2 | CFG_ZONE_V_SETPOINT |  | Range (0..65535) Lux
States the Lux set point.
See section 4.2.2 for a detailed description of accepted lux values.
53 | 2 | CFG_ZONE_DAYLIGHT |  | Range (0..65535) Lux
55 | 1 | CFG_ZONE_PRESENCE_LEVEL |  | Range (0..100) %
States the lux level (in %) for presence in the 2-Level function.
See section 4.2.2 for a detailed description of accepted lux values.
56 | 1 | CFG_ZONE_NON_PRESENCE_LEVEL |  | Range (0..100) %
States the lux level (in %)for non-presence in the 2-Level function.
57 | 1 | CFG_ZONE_ORIENTATION_LEVEL |  | Range (0..100) %
States the lux level (in %) for orientation light.
Not in Zone 5.
58 | 1 | CFG_ZONE_TURNON_LEVEL |  | Range (1..100) %, default:100
Not in Zone 5.
Zone 2
59 | 1 | CFG_ZONE_COMMON_FUNC1
60 | 1 | CFG_ZONE_ONOFF_FUNC2 |  | See decription for Zone 1
61 | 1 | CFG_ZONE_DALI_FUNC1
62 | 2 | CFG_ZONE_T_OFFPIR_DELAY
64 | 2 | CFG_ZONE_T_PRESENCE_DELAY
66 | 2 | CFG_ZONE_T_NON_PRESENCE_DELAY
68 | 2 | CFG_ZONE_T_ORIENTATION_DELAY
70 | 2 | CFG_ZONE_T_ON_DELAY
72 | 1 | CFG_ZONE_TYPE
73 | 1 | CFG_ZONE_RESERVED
74 | 2 | CFG_ZONE_DESKDAYLIGHTFACTORPCT
76 | 2 | CFG_ZONE_DESKMAXARTIFICIALLIGHT
78 | 2 | CFG_ZONE_V_SETPOINT
80 | 2 | CFG_ZONE_DAYLIGHT
82 | 1 | CFG_ZONE_PRESENCE_LEVEL
83 | 1 | CFG_ZONE_NON_PRESENCE_LEVEL
84 | 1 | CFG_ZONE_ORIENTATION_LEVEL
85 | 1 | CFG_ZONE_TURNON_LEVEL
Zone 3
86 | 1 | CFG_ZONE_COMMON_FUNC1
87 | 1 | CFG_ZONE_ONOFF_FUNC2 |  | See decription for Zone 1
88 | 1 | CFG_ZONE_DALI_FUNC1
89 | 2 | CFG_ZONE_T_OFFPIR_DELAY
91 | 2 | CFG_ZONE_T_PRESENCE_DELAY
93 | 2 | CFG_ZONE_T_NON_PRESENCE_DELAY
95 | 2 | CFG_ZONE_T_ORIENTATION_DELAY
97 | 2 | CFG_ZONE_T_ON_DELAY
99 | 1 | CFG_ZONE_TYPE
100 | 1 | CFG_ZONE_RESERVED
101 | 2 | CFG_ZONE_DESKDAYLIGHTFACTORPCT
103 | 2 | CFG_ZONE_DESKMAXARTIFICIALLIGHT
105 | 2 | CFG_ZONE_V_SETPOINT
107 | 2 | CFG_ZONE_DAYLIGHT
109 | 1 | CFG_ZONE_PRESENCE_LEVEL
110 | 1 | CFG_ZONE_NON_PRESENCE_LEVEL
111 | 1 | CFG_ZONE_ORIENTATION_LEVEL
112 | 1 | CFG_ZONE_TURNON_LEVEL
Zone 4
113 | 1 | CFG_ZONE_COMMON_FUNC1
114 | 1 | CFG_ZONE_ONOFF_FUNC2 |  | See decription for Zone 1
115 | 1 | CFG_ZONE_DALI_FUNC1
116 | 2 | CFG_ZONE_T_OFFPIR_DELAY
118 | 2 | CFG_ZONE_T_PRESENCE_DELAY
120 | 2 | CFG_ZONE_T_NON_PRESENCE_DELAY
122 | 2 | CFG_ZONE_T_ORIENTATION_DELAY
124 | 2 | CFG_ZONE_T_ON_DELAY
126 | 1 | CFG_ZONE_TYPE
127 | 1 | CFG_ZONE_RESERVED
128 | 2 | CFG_ZONE_DESKDAYLIGHTFACTORPCT
130 | 2 | CFG_ZONE_DESKMAXARTIFICIALLIGHT
132 | 2 | CFG_ZONE_V_SETPOINT
134 | 2 | CFG_ZONE_DAYLIGHT
136 | 1 | CFG_ZONE_PRESENCE_LEVEL
137 | 1 | CFG_ZONE_NON_PRESENCE_LEVEL
138 | 1 | CFG_ZONE_ORIENTATION_LEVEL
139 | 1 | CFG_ZONE_TURNON_LEVEL
Zone 5
140 | 1 | CFG_ZONE_COMMON_FUNC1
141 | 1 | CFG_ZONE_ONOFF_FUNC2 |  | See decription for Zone 1
142 | 1 | CFG_ZONE_DALI_FUNC1
143 | 2 | CFG_ZONE_T_OFFPIR_DELAY
145 | 2 | CFG_ZONE_T_PRESENCE_DELAY
147 | 2 | CFG_ZONE_T_NON_PRESENCE_DELAY
149 | 2 | CFG_ZONE_T_ORIENTATION_DELAY
151 | 2 | CFG_ZONE_T_ON_DELAY
153 | 1 | CFG_ZONE_TYPE
154 | 1 | CFG_ZONE_RESERVED
155 | 2 | CFG_ZONE_DESKDAYLIGHTFACTORPCT
157 | 2 | CFG_ZONE_DESKMAXARTIFICIALLIGHT
159 | 2 | CFG_ZONE_V_SETPOINT
161 | 2 | CFG_ZONE_DAYLIGHT
163 | 1 | CFG_ZONE_PRESENCE_LEVEL
164 | 1 | CFG_ZONE_NON_PRESENCE_LEVEL
165 | 1 | CFG_ZONE_ORIENTATION_LEVEL
166 | 1 | CFG_ZONE_TURNON_LEVEL
1.1.3 0x010D - SetUserConfig
With this telegram, the app can configure each zone/channel. This telegram contains parameters for all sensor variants.
The telegram can also be used to set Factory settings for a specific country.
· If Config State is set to 255, then this tells the sensor, that the user has made changes to the user configuration.
· If Config State is set to a number between 1..254, then the telegram is handled as a factory reset command towards the sensor. All parameter settings in this telegram will then be stored as factory setting in the sensor.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetUserConfig Id
3 | 2 | Total Length | 0xA7 | Total length of 167 bytes
5 | 2 | CRC16 | ToBeCalc | Calculated value, see section 4.5
7 | 160 | See definition from Byte no. 7 in section 4.4.12
1.1.4 0x010E - SetUserConfigReply
This telegram requests Sensor Configuration from the sensor which is currently connected.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetUserConfig Id
3 | 2 | Total Length | 0x08 | Total length of 8 bytes
5 | 2 | CRC16 | 0x2807 | Calculated value, see section 4.5
7 | 1 | Result | 0x00 | Reply result:
0 = ACK – UserConfig validated OK and stored with success
1 = NACK_RANGE_CHECK – A UserConfig parameter has invalid range
2 = NACK_NVM – Saving to Non Volatile Memory failed
3 = NACK_FRAME_SIZE_ERROR – Wrong Frame size.
8 = NACK_OPENPERIOD_OVER – Open Period Over
1.1.5 0x0111 - SetWiredPushButtonList
This telegram is used to configure all Wired Push Buttons.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetWiredPushButtonList Id
3 | 2 | Total Length | 0x1C | Total length of 28 bytes
5 | 2 | CRC16 | 0x28F9 | Calculated value, see section 4.5
7 | 1 | Version | 0x02 | Holds the current version of the Wired push Button list.
Range(2)
8 | 5 | WiredPushButton 1 |  | See section 4.2.7 for more details.
13 | 5 | WiredPushButton 2 |  | If Config Type = 0, this will delete the entry.
18 | 5 | WiredPushButton 3
23 | 5 | WiredPushButton 4
1.1.6 0x0112 - SetWiredPushButtonListReply
This telegram is a reply for the SetWiredPushButtonList telegram.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetWiredPushButtonListReply Id
3 | 2 | Total Length | 0x08 | Total length of 8 bytes
5 | 2 | CRC16 | 0x7C92 | Calculated value, see section 4.5
7 | 1 | Result |  | Reply result:
0 = ACK – WiredPBList validated OK and stored with success
1 = NACK_RANGE_CHECK – A WiredPBList parameter has invalid range
2 = NACK_NVM – Saving to Non Volatile Memory failed
3 = NACK_FRAME_SIZE_ERROR – Wrong Frame size.
8 = NACK_OPENPERIOD_OVER – Open Period Over
1.1.7 0x0113 - GetWiredPushButtonList
This telegram is used to retrieve the complete Wired Push Button list from the sensor.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetWiredPushButtonList Id
3 | 2 | Total Length | 0x07 | Total length of 7 bytes
5 | 2 | CRC16 | 0x1A18 | Calculated value, see section 4.5
1.1.8 0x0114 - GetWiredPushButtonListReply
This telegram is a reply for the GetWiredPushButtonList telegram.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetWiredPushButtonConfigReply Id
3 | 2 | Total Length | 0x1C | Total length of 28 bytes
5 | 2 | CRC16 | 0x94BC | Calculated value, see section 4.5
7 | 1 | Version | 0x02 | Holds the current version of the Wired push Button list.
Range(2)
8 | 5 | WiredPushButton 1 |  | See section 4.2.7 for more details
13 | 5 | WiredPushButton 2
18 | 5 | WiredPushButton 3
23 | 5 | WiredPushButton 4
1.1.9 0x0119 - SetBLEPushButtonList
This telegram is used to configure all BLE Push Buttons.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetBLEPushButtonList Id
3 | 2 | Total Length | 0x64 | Total length of 100 bytes
5 | 2 | CRC16 | 0x646B | Calculated value, see section 4.5
7 | 1 | Version | 0x02 | Holds the current version of the Wireless push Button list.
Range(2)
8 | 23 | BLE PushButton 1 |  | See section 4.2.9 for more details
31 | 23 | BLE PushButton 2
54 | 23 | BLE PushButton 3
77 | 23 | BLE PushButton 4
1.1.10 0x0120 - SetBLEPushButtonListReply
This telegram is a reply for the SetBLEPushButtonList telegram.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetBLEPushButtonListReply Id
3 | 2 | Total Length | 0x08 | Total length of 8 bytes
5 | 2 | CRC16 | 0x37C9 | Calculated value, see section 4.5
7 | 1 | Result |  | Reply result:
0 = ACK – BLEPBList validated OK and stored with success
1 = NACK_RANGE_CHECK – A BLEPBList parameter has invalid range
2 = NACK_NVM – Saving to Non Volatile Memory failed
3 = NACK_FRAME_SIZE_ERROR – Wrong Frame size.
8 = NACK_OPENPERIOD_OVER – Open Period Over
1.1.11 0x0121 - GetBLEPushButtonList
This telegram is used to retrieve the complete BLE Push Button list from the sensor.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetBLEPushButtonList Id
3 | 2 | Total Length | 0x07 | Total length of 7 bytes
5 | 2 | CRC16 | 0xDB99 | Calculated value, see section 4.5
1.1.12 0x0122 - GetBLEPushButtonListReply
This telegram is a reply for the GetBLEPushButtonList telegram.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetBLEPushButtonConfigReply Id
3 | 2 | Total Length | 0x64 | Total length of 100 bytes
5 | 2 | CRC16 | ToBeCalc | Calculated value, see section 4.5
7 | 1 | Version | 0x02 | Holds the current version of the Wireless push Button list.
Range(2)
8 | 23 | BLE PushButton 1 |  | See section 4.2.9 for more details
31 | 23 | BLE PushButton 2
54 | 23 | BLE PushButton 3
77 | 23 | BLE PushButton 4
1.1.13 0x013D - SetDaliPushButtonList
This telegram is used to configure all Dali Push Buttons.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetDaliPushButtonList Id
3 | 2 | Total Length | 0x6C | Total length of 108 bytes
5 | 2 | CRC16 | 0x107D | Calculated value, see section 4.5
7 | 1 | Version | 0x04 | Holds the current version of the Dali Push Button list.
Range(3)
8 | 25 | Dali PushButton 1 |  | See section 4.2.9 for more details
33 | 25 | Dali PushButton 2
58 | 25 | Dali PushButton 3
83 | 25 | Dali PushButton 4
1.1.14 0x013E - SetDaliPushButtonListReply
This telegram is a reply for the SetDaliPushButtonList telegram.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | SetDaliPushButtonListReply Id
3 | 2 | Total Length | 0x08 | Total length of 8 bytes
5 | 2 | CRC16 | 0x04EE | Calculated value, see section 4.5
7 | 1 | Result |  | Reply result:
0 = ACK – BLEPBList validated OK and stored with success
1 = NACK_RANGE_CHECK – A BLEPBList parameter has invalid range
2 = NACK_NVM – Saving to Non Volatile Memory failed
3 = NACK_FRAME_SIZE_ERROR – Wrong Frame size.
8 = NACK_OPENPERIOD_OVER – Open Period Over
1.1.15 0x013F - GetDaliPushButtonList
This telegram is used to retrieve the complete Dali Push Button list from the sensor.
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetDaliPushButtonList Id
3 | 2 | Total Length | 0x07 | Total length of 7 bytes
5 | 2 | CRC16 | 0x6364 | Calculated value, see section 4.5
1.1.16 0x0140 - GetDaliPushButtonListReply
This telegram is a reply for the GetDaliPushButtonList telegram.
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | GetDaliPushButtonConfigReply Id
3 | 2 | Total Length | 0x6C | Total length of 108 bytes
5 | 2 | CRC16 | 0x6B8E | Calculated value, see section 4.5
7 | 1 | Version | 0x03 | Holds the current version of the Dali Push Button list.
Range(3)
8 | 25 | Dali PushButton 1 |  | See section 4.2.9 for more details
33 | 25 | Dali PushButton 2
58 | 25 | Dali PushButton 3
83 | 25 | Dali PushButton 4

## DALI-102_Commands_for_settings
1.1.1 0x0411 - DaliSetDevicesMaxLevel
This telegram sets the common device parameter MAX LEVEL in the database and in all connected control gear on the bus
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceMaxLevel Id
3 | 2 | Total Length | 0x08 | Total Length of 8 bytes
5 | 2 | CRC16 | 0x0CBE | Calculated value, see section 4.5
7 | 1 | MaxLevel |  | Range: 0x00 – 0xFE ( 0-254 )
1.1.2 0x042E - DaliSetDeviceMaxLevelReply
This telegram is a reply for the DaliSetDeviceMaxLevel telegram
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceMaxLevelReply Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0xC788 | Calculated value, see section 4.5
7 | 1 | Status | 0x00 | ACK = 0
- validated OK.
NACK_COMMISSIONING_RUNNING = 3
- Commissioning running
8 | 1 | Data | 0x00 | Not used
1.1.3 0x0412 - DaliSetDevicesMinLevel
This datatype sets the common device parameter MIN LEVEL in the database and in all connected control gear on the bus
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceMinLevel Id
3 | 2 | Total Length | 0x08 | Total Length of 8 bytes
5 | 2 | CRC16 | 0x9762 | Calculated value, see section 4.5
7 | 1 | MinLevel |  | Range: 0x00 – 0xFE ( 0-254 )
1.1.4 0x042F - DaliSetDeviceMinLevelReply
This telegram is a reply for the DaliSetDeviceMinLevel telegram
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceMinLevelReply Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0xB13C | Calculated value, see section 4.5
7 | 1 | Status | 0x00 | ACK = 0 - validated OK.
NACK_COMMISSIONING_RUNNING = 3
- Commissioning running
8 | 1 | Data | 0x00 | Not used
1.1.5 0x0413 - DaliSetDevicesPowerOnLevel
This datatype sets the common device parameter POWER ON LEVEL in the database and in all connected control gear on the bus
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDevicePowerOn Id
3 | 2 | Total Length | 0x08 | Total Length of 8 bytes
5 | 2 | CRC16 | 0xE1D6 | Calculated value, see section 4.5
7 | 1 | PowerOnLevel |  | Range: 0x00 – 0xFF (0-255)
255 = highest lightLevel
1.1.6 0x0430 - DaliSetDevicePowerOnReply
This telegram is a reply for the DaliSetDevicePowerOn telegram
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDevicePowerOnReply Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0x7E75 | Calculated value, see section 4.5
7 | 1 | Status | 0x00 | ACK = 0
- validated OK.
NACK_COMMISSIONING_RUNNING = 3
- Commissioning running
8 | 1 | Data | 0x00 | Not used
1.1.7 0x0414 - DaliSetDevicesSysFailLevel
This datatype sets the common device parameter SYSTEM FAILURE LEVEL in the database and in all connected control gear on the bus
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceSysFailLevel Id
3 | 2 | Total Length | 0x08 | Total Length of 8 bytes
5 | 2 | CRC16 | 0xB0FB | Calculated value, see section 4.5
7 | 1 | SysFailLevel |  | Range: 0x00 – 0xFF (0-255)
255 = no change in system level
1.1.8 0x0431 - DaliSetDeviceSysFailLevelReply
This telegram is a reply for the DaliSetDeviceSysFailLevel telegram
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceSysFailLevelReply Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0x08C1 | Calculated value, see section 4.5
7 | 1 | Status | 0x00 | ACK = 0 - validated OK.
NACK_COMMISSIONING_RUNNING = 3
- Commissioning running
8 | 1 | Data | 0x00 | Not used
1.1.9 0x0415 - DaliSetDevicesFadeTime
This datatype sets the common device parameter FADE TIME in the database and in all connected control gear on the bus
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceFadeTime Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0xC64F | Calculated value, see section 4.5
7 | 1 | FadeTime |  | Range: 0x00 – 0x0F (0-15). (See Table 4)
8 | 1 | ExtendedFadeTime |  | Range: 0x00 – 0x4F (0-79)
Bitwise: 0YYYAAAAb
YYY = fade time multiplier. (See Table 7)
AAAA = fade time base. (See Table 6)
1.1.10 0x0432 - DaliSetDeviceFadeTimeReply
This telegram is a reply for the DaliSetDeviceFadeTime telegram
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceFadeTimeReply Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0x931D | Calculated value, see section 4.5
7 | 1 | Status | 0x00 | ACK = 0
- validated OK.
NACK_RANGE_CHECK = 1
- parameter has invalid range.
NACK_COMMISSIONING_RUNNING = 3
- Commissioning running
8 | 1 | Data | 0x00 | Not used
1.1.11 0x0416 - DaliSetDevicesFadeRate
This datatype sets the common device parameter FADE RATE in the database and in all connected control gear on the bus
BLE device -> Sensor
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceFadeRate Id
3 | 2 | Total Length | 0x08 | Total Length of 8 bytes
5 | 2 | CRC16 | 0x5D93 | Calculated value, see section 4.5
7 | 1 | FadeRate |  | Range: 0x01 – 0x0F (1-15). (See Table 5)
1.1.12 0x0433 - DaliSetDeviceFadeRateReply
This telegram is a reply for the DaliSetDeviceFadeTime telegram
Sensor -> BLE device
Byte | Field | Field | Example | Example
no. | Size | Description |  | Description
0 | 1 | Protocol Version | 0x01 | Protocol Id
1 | 2 | Telegram Type |  | DaliSetDeviceFadeRateReply Id
3 | 2 | Total Length | 0x09 | Total Length of 9 bytes
5 | 2 | CRC16 | 0xE5A9 | Calculated value, see section 4.5
7 | 1 | Status | 0x00 | ACK = 0 - validated OK.
NACK_RANGE_CHECK = 1
- parameter has invalid range.
NACK_COMMISSIONING_RUNNING = 3
- Commissioning running
8 | 1 | Data | 0x00 | Not used